## Slide 1
PROCESSI PER IL RECUPERO DI BIOPOLIMERI DAI FANGHI DI DEPURAZIONE
Nicola Frison1, Francesco Fatone2
1University of Verona, Department of Biotechnology
2Polytechnic University of Marche, Department of Materials, Environmental and City planning Science and Engineering

## Slide 2: Objective
Horizon 2020 Smart-Plant project
Volatile Fatty Acids (VFAs) production as PHAs precursors;
Strategy for integrated PHA production in WWTP;
PHA productivity and barriers

## Slide 3
This report on the bioeconomy addresses circularity aspects of bio-based products and the sustainable use of renewable natural resources.
5 priority areas:
Plastics;
Food waste
Critical raw materials (e.g., P);
Construction and demolition waste;
Biomass and bio-based products

## Slide 4
Potential for 300 new biorefinery;
Address interface between chemical, product and waste legislation;
R&D: 100 M€ (e.g. Horizon2020).

## Slide 5: Horizon 2020 – Smart-plant project
Biocomposites
Organic
compounds

## Slide 6
- Il 30-35% dei solidi sospesi nell’acqua reflua sono costituiti da cellulosa (carta igienica). Di questi, meno del 30% viene trattenuto dalla separazione primaria;
- Il 60% del materiale cellulosico viene degradato nel processo a fanghi attivi;
- La cellulosa non è COD rapidamente biodegradabile;
Separazione a monte della frazione cellulosica al fine di convertirla in carbonio funzionale al processo biologico (VFAs)

## Slide 7: Biorefinery of Cellulosic Primary Sludge (CPS)
Up to 10 Kg/PE y
(Ruiken et al., 2013)
Crutchik et al., 2018

## Slide 8: SCEPPHAR: process configuration
Biological nutrients removal
Municipal wastewater
Effluent
Anaerobic Digestion
Fermentation of cellulosic sewage sludge
Solid Stream
Anaerobic Supernatant
Aerobic/Anoxi feast/famine
SBR
PHA recovery
Treated anaerobic supernatant
Sludge recycle
Separation
VFAs
Liquid Stream
Cellulosic primary sludge
Waste Activated Sludge
Biogas
Batch for PHA accumulation
VFAs
4° step
2° step
5° step
Selected biomass
WW Microscreen (350 μm)
Struvite
Mg(OH)2
1° step
Nitritation
SBR
3° step
Frison et al., 2015

## Slide 10: Rotating belt filter for CPS recovery
Fine mesh size: 350 µm
Wastewater Flowrate: 29-40 m3/h
Fixed surface contact area: 0.24 m2
Variable belt rotation speed
Average TSS removal = 45-50%

## Slide 11: Effect of the mesh size
Chart: TSS loading rate [kgTSS/m2/h]
| 22.072499999999955 | 44.689999999999991 | 21.255000000000042 | 30.09 | 26.550000000000018 | 38.940000000000047 | 36.60833333333337 | 31.27999999999999 | 23.299166666666672 | 27.270000000000032 | 33.49833333333337 | 35.595000000000013 | 18.666666666666647 | 23.391666666666687 | 38.836666666666716
350 um + polymer | 48.1481 | 57.9268 | 39.7436 | 55.8824 | 46.6667 | 44.697 | 40 | 53.125 | 58.9041 | 54.321 | 37.6686 | 50.495 | 40.708 | 45.7143 | 34.2857 | 40.1639
350 um | 43.75 | 37.9845 | 22.5806 | 76 | 26.1364 | 35.0649 | 49.5726 | 53.0201 | 22.7273 | 17.0732 | 48.4848 | 60.8696 | 76 | 43.6681
210 um | 38.0952 | 44.5783 | 38.6667 | 22.4138 | 50.5376 | 58.6957 | 41.9753 | 26.0274 | 28.6099 | 54.1283 | 58.3454 | 43.038 | 38.5714 | 45.5696 | 40 | 42.5287
The mesh size does not affect significantly the removal efficiency
Polymer should enhance the formation of strong sludge flocs

## Slide 12: Fermentation unit for SCFAs recovery from CPS
Volume: 2.6 m3
Operating Temperature: 37°C
HRT: 4-6 days
Probe for the monitoring of the influent TSS concentration

## Slide 13: Short-Cut Enhanced Phosphorus and PHA recovery (SCEPPHAR)
Nitritation SBR
PHA accumulation
Crystallizer
Biomass selection SBR
Equalization tank
Ceramic membrane

## Slide 14: Characteristics of Cellulosic Primary Sludge (CPS)
Cellulose: 31 - 51%
Lignin: 14 - 20%
Hemicellulose: 4,2 - 5,9
Lipids: 6.1 – 12%
Proteins: 1- 12% (Low content of nitrogen released during the fermentation)
Ashes: 4 - 11.5%
Cellulosic Primary Sludge after cleaning and drying

## Slide 15: Characteristics of the fermentation liquid
Observed VFAs yield around 0.32-0.38 gCODVFA/gVSSfed
COD:N:P ratio in the liquid fraction ~ 133:2.7:1
Phosphorus (and fraction of ammonia) recovered as P salts forms
Parameter | Unit | Average | Min | Max
pH | - | 4.9 | 4.8 | 5.0
VFAs | mgCOD/L | 9975 | 8134 | 12146
NH4-N | mgN/L | 198 | 164 | 307
PO4-P | mgP/L | 75 | 44 | 82

## Slide 16: Nitritation SBR
Period 1: not heated; Period 2 and 3: heated;
In Period 2 and 3 the vNLR was increased up to 1.55-1.70 kgN/m3d (T = 25-30°C), SRT 20 giorni.
In Period 2 and 3 the observed nitritation rate was 55-65 mgN/L h, 80-90% of ammonia was oxidized to nitrite

## Slide 17: Selection SBR
Feast/Famine ratio was 0.06 – 0.15 min/min
HRT: 1.0-1.5 day
OLR: 1.7-2.0 kgCOD/m3 day
Chart: P1 P2 P3
 | 0 | 2000 | 0 | 2000 | 0 | 2000 | 0 | 2000

## Slide 18: Selection SBR
Chart: P1 P2 P3
 | 0 | 2000 | 0 | 2000 | 0 | 2000 | 0 | 2000
Optimal PHA biomass selection when
Feast/Famine < 0,2 min/min
Feast/Famine ratio was 0.06 – 0.15 min/min
HRT: 1.0-1.5 day
OLR: 1.7-2.0 kgCOD/m3 day

## Slide 19: Typical cycle of the selection SBR (aerobic/anoxic)
Chart: Aerobic (feast) Anoxic (famine)
| 0 | 5.9999999999999787 | 12.000000000000011 | 21.600000000000019 | 35 | 50.399999999999991 | 60 | 87.6 | 163.80000000000001 | 234 | 300 | 344.40000000000003
DO | 0.4 | 0.5 | 0.8 | 0.48 | 0.25 | 4.4 | 2 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
NO2-N | 0 | 6
 | 9.19 | 9.25 | 9.18 | 9.2 | 9.25 | 9.29 | 9.29 | 9.3
NO2-N | 37.34 | 8.39 | 5.27 | 1.73 | 124.1782 | 99 | 75 | 55 | 42 | 32
VFA | 295.8281 | 161.781 | 27.7339 | 0
PHA | 80 | 160.0328 | 240.0657 | 256.6242 | 256.6242 | 230.6922 | 205.9736 | 185.3748 | 171.9856 | 161.6862
Period 1: acetic acid as carbon source (as reference);
Period 2 and 3: fermentation liquid from CPS as carbon source;
Nitrite removal efficiency around 85%;
The kd (@20°C) was 10-12 mgN/gVSS h (driven by PHA degradation);

## Slide 20: PHA accumulation
Chart: Time (h)
| 0 | 0.96666666666666667 | 2 | 3 | 3.9166666666666665 | 4.7333333333333334 | 5.5666666666666664 | 6.25
% PHA | 0.049446 | 0.18102 | 0.27233 | 0.27377 | 0.37879 | 0.42241
Chart: Yield (gPHA/gCODVFA); % of PHA (gPHA/gMLSS x 100)
| Acetic Acid | CPS fermentation liquid
Yield PHA/VFA | 0.35333 | 0.34
%PHA | 0.49093 | 0.47651

## Slide 21: Mass balance of the system
Wastewater Sieving
Fermentation
Efficiency
0,32-0,38 gCODVFA/gVSS
Municipal Wastewater
(adapted from Metcalf&Eddy, 2013)
25-30 kgSS/PE y
4 kgN/PE year
CPS
13-14 kgSS/PE y
Sieved Wastewater
13-15 kgSS/PE y
~ 4 kgN/PE year
To mainstream wastewater treatment
Nitritation and Selection SBRs:
YX/VFA = 0.31 gVSS/gCODVFA
Accumulation PHA
YPHA/VFA = 0.36-0.42 gPHA/gCODVFA
To biogas
production
Nitrogen from reject water
~ 0.4 kgN/PE y
VFAs
5.0-5.5 kgCOD/PE y
Treated reject water
~ 0.06 kgN/PE y
PHA
~ 1 kgPHA/PE y

## Slide 22: PHA extraction and purification: sustainable?
Final dry solids
Thanks to Bruno Ferreira (Biotrend SA, Portugal)
Polymer film produced after chloroform extraction and ethanol washing

## Slide 23: PHA Extraction: mass balance
Chemical extraction: around 0,15 kgNaCl/kgPHA + 0,27 kgNaOH/kgPHA
N & P released during the extraction needs to be treated!!!!

## Slide 24: Estimated cost of chemicals for PHA extraction: cheap and/or green?
- Extraction recovery efficiency: 75-85%
Purity of the extracted PHA: > 95%
Total cost (only for chemicals, mainly NaOH, NaClO, H2O2):
- 0,9-1,2 €/kgPHA extracted (currently very affected by the scale of the process)
- SDS-Sodium hypochlorite: 0.29 €/kgPHA extracted (CalRecycle, 2013)
Thanks to Bruno Ferreira (Biotrend SA, Portugal)

## Slide 25
Dried accumulated PHA Biomass + 20% of PHBV
Dried accumulated PHA Biomass + 20% of PE
Dried accumulated PHA Biomass
(105°C for 24 h)
Strenghtness of the biocomposites
10 cm
10 cm
10 cm
First biocomposites from raw PHA accumulated biomass
Thanks to Yonghui Zhou (Brunel University, UK) & Ecodek (UK)

## Slide 26: Conclusions
Cellulosic primary sludge is suitable for the production of VFAs (0.32-0.38 gCODVFA/gVSS);
The SCEPPHAR system can be integrated in the sludge line for PHA production combined with the treatment of reject water from anaerobic sludge digestion;
The overall nitrogen removal efficiency is around 80-85%;
The PHA recovery potential is around 1 kgPHA / PE year (around 10% of the sludge production)

## Slide 27
THANK YOU FOR YOUR ATTENTION!

## Slide 28: Objectives
Recovery of cellulosic primary sludge (CPS) through dynamic rotating belt filter;
Long-term operation of the Short-cut Enhanced Phosphorus and PHA recovery pilot plant at the Carbonera WWTP (owned by Alto Trevigiano Servizi Srl);
Selection of PHA storing bacteria during the via-nitrite nitrogen removal from anaerobic supernatant (aerobic feast and anoxic famine);
Mass balance of the system and recovered (organics) resources

## Slide 29: Outline
The world needs new resources…from wastewater;
The water industry consumes about 1% of the overall electricity (Caldwell, 2009; 2° Eur Water and Wastewater Conf);
Activated sludge is the major energy consumer (∼55% of the energy use);
The water factory concept of the future: «Not Dissipate» but «Upgrade» low cost carbon source into high added value bioproducts (IWA Resource Recovery Cluster, 2016).